## Sheet3
SUMMARY OUTPUT
Regression Statistics
Multiple R | 0.98126
R Square | 0.96287
Adjusted R Square | 0.9443
Standard Error | 0.32945
Observations | 4
ANOVA
| df | SS | MS | F | Significance F
Regression | 1 | 5.6286 | 5.6286 | 51.8598 | 0.018742
Residual | 2 | 0.21707 | 0.10853
Total | 3 | 5.8457
| Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
Intercept | -2.892 | 0.68315 | -4.2333 | 0.051526 | -5.8314 | 0.047378 | -5.8314 | 0.047378
0.15625 | 16.976 | 2.3573 | 7.2014 | 0.018742 | 6.8332 | 27.1188 | 6.8332 | 27.1188
RESIDUAL OUTPUT |  |  |  |  | PROBABILITY OUTPUT
Observation | Predicted 0.26 | Residuals | Standard Residuals |  | Percentile | 0.26
1 | 0.291 | 0.239 | 0.8885 |  | 12.5 | 0.53
2 | 1.352 | -0.252 | -0.93683 |  | 37.5 | 1.1
3 | 2.413 | -0.213 | -0.79185 |  | 62.5 | 2.2
4 | 3.474 | 0.226 | 0.84017 |  | 87.5 | 3.7

## Table 1
Catalog OEM-3, Distributors and Flow Controls / Page 5
Distributor Tube Circuit Capacity Table — Tons of Refrigeration
Tube Size inches O.D. | Refrigerant
| R-12 / R-134a | [5 empty] | R-22 | [8 empty] | R-404A / R-502 / R-507 | [7 empty] | R-410A
Evaporating Temperature °F
| 40° | 20° | 0° | -20° |  | -40° | 40° |  | 20° |  | 0° |  | -20° | -40° |  | 40° | 20° |  | 0° |  | -20° |  | -40° | 40° |  |  | 20° |  | 0° | -20° |  | -40°
5/32 | 0.19 | 0.14 | 0.11 | 0.08 |  | 0.06 | 0.26 |  | 0.21 |  | 0.16 |  | 0.12 | 0.09 |  | 0.18 | 0.13 |  | 0.1 |  | 0.07 |  | 0.05 | — |  |  | — |  | — | — |  | —
3/16 | 0.4 | 0.3 | 0.23 | 0.17 |  | 0.13 | 0.53 |  | 0.44 |  | 0.33 |  | 0.24 | 0.2 |  | 0.37 | 0.28 |  | 0.22 |  | 0.15 |  | 0.12 | 0.42 |  |  | 0.31 |  | 0.23 | 0.18 |  | 0.14
1/4 | 0.8 | 0.6 | 0.45 | 0.33 |  | 0.25 | 1.1 |  | 0.89 |  | 0.67 |  | 0.49 | 0.39 |  | 0.73 | 0.58 |  | 0.43 |  | 0.31 |  | 0.23 | 1.21 |  |  | 0.9 |  | 0.68 | 0.52 |  | 0.4
5/16 | 1.6 | 1.2 | 0.9 | 0.66 |  | 0.5 | 2.2 |  | 1.7 |  | 1.3 |  | 0.98 | 0.79 |  | 1.5 | 1.1 |  | 0.83 |  | 0.62 |  | 0.46 | 2.46 |  |  | 1.83 |  | 1.39 | 1.06 |  | 0.81
3/8 | 2.8 | 2.1 | 1.6 | 1.2 |  | 0.88 | 3.7 |  | 2.9 |  | 2.2 |  | 1.7 | 1.4 |  | 2.5 | 2 |  | 1.5 |  | 1.1 |  | 0.8 | 4.44 |  |  | 3.32 |  | 2.51 | 1.91 |  | 1.47
Refrigerants at various evaporator temperatures - Tons of Refrigeration
Capacity per circuit at 10 psi pressure drop. See Distributor Loading vs. Pressure Drop table below for pressure drop at 50% to 200% of this rating.
*Correction Factors for Other Liquid Temperatures for Nozzle and Tubes
Liquid Temperature °F |  |  |  |  | 50° |  |  | 60° |  |  |  | 70° |  |  | 80° |  |  | 90° |  |  |  | 100° |  |  |  | 110° |  |  |  | 120°
Correction factor |  |  |  |  | 2.1 |  |  | 1.83 |  |  |  | 1.59 |  |  | 1.37 |  |  | 1.17 |  |  |  | 1 |  |  |  | 0.85 |  |  |  | 0.72
**Correction Factors for Other Distributor Tube Lengths
Tube Length – Inches |  |  |  |  | 12 |  | 18 |  |  | 24 |  |  | 30 |  | 36 |  | 42 |  |  | 48 |  |  | 54 |  | 60 |  |  |  | 66 |  | 72
Correction Factor |  |  |  |  | 1.36 |  | 1.16 |  |  | 1.07 |  |  | 1 |  | 0.95 |  | 0.9 |  |  | 0.86 |  |  | 0.82 |  | 0.79 |  |  |  | 0.76 |  | 0.73
*100°F liquid entering thermostatic expansion valve.
**For tubing length of 30"
Distributor Loading vs. Pressure Drop
Actual Load as a Percent of Published Rating (corrected for Liquid Temperature and/or Tube Length if needed) | [8 empty] | R-12 / R-134a | [11 empty] | R-22
[9 empty] |  P Nozzle (psi) | [5 empty] |  P Tubes and Passages (psi) | [5 empty] |  P Nozzle (psi) | [6 empty] |  P Tubes and Passages (psi)
50 | [8 empty] | 4 | [5 empty] | 3 | [5 empty] | 7 | [6 empty] | 3
60 | [8 empty] | 6 | [5 empty] | 4 | [5 empty] | 10 | [6 empty] | 4
70 | [8 empty] | 8 | [5 empty] | 5 | [5 empty] | 13 | [6 empty] | 5
80 | [8 empty] | 10 | [5 empty] | 6 | [5 empty] | 16 | [6 empty] | 6
90 | [8 empty] | 12 | [5 empty] | 8 | [5 empty] | 20 | [6 empty] | 8
100 | [8 empty] | 15 | [5 empty] | 10 | [5 empty] | 25 | [6 empty] | 10
110 | [8 empty] | 18 | [5 empty] | 12 | [5 empty] | 30 | [6 empty] | 12
120 | [8 empty] | 20 | [5 empty] | 14 | [5 empty] | 35 | [6 empty] | 14
130 | [8 empty] | 22 | [5 empty] | 16 | [5 empty] | 38 | [6 empty] | 16
140 | [8 empty] | 24 | [5 empty] | 18 | [5 empty] | 40 | [6 empty] | 18
150 | [8 empty] | 27 | [5 empty] | 21 | [5 empty] | 43 | [6 empty] | 21
160 | [8 empty] | 29 | [5 empty] | 23 | [5 empty] | 46 | [6 empty] | 24
170 | [8 empty] | 31 | [5 empty] | 25 | [5 empty] | 49 | [6 empty] | 27
180 | [8 empty] | 33 | [5 empty] | 27 | [5 empty] | 52 | [6 empty] | 30
190 | [8 empty] | 36 | [5 empty] | 29 | [5 empty] | 54 | [6 empty] | 32
200 | [8 empty] | 38 | [5 empty] | 31 | [5 empty] | 57 | [6 empty] | 34
Actual Load as a Percent of Published Rating (corrected for Liquid Temperature and/or Tube Length if needed) | [8 empty] | R-404A / R-502 / R-507 | [11 empty] | R-410A
[9 empty] |  P Nozzle (psi) | [5 empty] |  P Tubes and Passages (psi) | [5 empty] |  P Nozzle (psi) | [6 empty] |  P Tubes and Passages (psi)
50 | [8 empty] | 7 | [5 empty] | 3 | [5 empty] | 12 | [6 empty] | 3
60 | [8 empty] | 10 | [5 empty] | 4 | [5 empty] | 17 | [6 empty] | 4
70 | [8 empty] | 13 | [5 empty] | 5 | [5 empty] | 21 | [6 empty] | 6
80 | [8 empty] | 16 | [5 empty] | 6 | [5 empty] | 26 | [6 empty] | 7
90 | [8 empty] | 20 | [5 empty] | 8 | [5 empty] | 30 | [6 empty] | 9
100 | [8 empty] | 25 | [5 empty] | 10 | [5 empty] | 35 | [6 empty] | 10
110 | [8 empty] | 30 | [5 empty] | 12 | [5 empty] | 40 | [6 empty] | 12
120 | [8 empty] | 35 | [5 empty] | 14 | [5 empty] | 44 | [6 empty] | 13
130 | [8 empty] | 38 | [5 empty] | 16 | [5 empty] | 49 | [6 empty] | 15
140 | [8 empty] | 40 | [5 empty] | 18 | [5 empty] | 53 | [6 empty] | 16
150 | [8 empty] | 43 | [5 empty] | 21 | [5 empty] | 58 | [6 empty] | 18
160 | [8 empty] | 46 | [5 empty] | 24 | [5 empty] | 62 | [6 empty] | 20
170 | [8 empty] | 49 | [5 empty] | 27 | [5 empty] | 67 | [6 empty] | 21
180 | [8 empty] | 52 | [5 empty] | 30 | [5 empty] | 71 | [6 empty] | 23
190 | [8 empty] | 54 | [5 empty] | 32 | [5 empty] | 76 | [6 empty] | 25
200 | [8 empty] | 57 | [5 empty] | 34 | [5 empty] | 80 | [6 empty] | 26

## Sheet2
SUMMARY OUTPUT
Regression Statistics
Multiple R | 0.97847
R Square | 0.9574
Adjusted R Square | 0.94319
Standard Error | 0.33604
Observations | 5
ANOVA
| df | SS | MS | F | Significance F
Regression | 1 | 7.6129 | 7.6129 | 67.4151 | 0.0037811
Residual | 3 | 0.33878 | 0.11293
Total | 4 | 7.9517
| Coefficients | Standard Error | t Stat | P-value | Lower 95% | Upper 95% | Lower 95.0% | Upper 95.0%
Intercept | -2.3925 | 0.50407 | -4.7464 | 0.017742 | -3.9967 | -0.78834 | -3.9967 | -0.78834
X Variable 1 | 15.4166 | 1.8776 | 8.2107 | 0.0037811 | 9.4411 | 21.392 | 9.4411 | 21.392

## Sheet1
Distributor Tube Circuit Capacity Table — Tons of Refrigeration
Tube Size inches O.D. | Refrigerant | [19 empty] | qt = qstd*kliq*klength*kevap*kref
| R-12 / R-134a |  |  |  |  | R-22 |  |  |  |  | R-404A / R-502 / R-507 |  |  |  |  | R-410A
| Evaporating Temperature °F | [19 empty] | qstd = std rating at 40 deg and 100 deg liquid; function of outlet size
| 40° | 20° | 0° | -20° | -40° | 40° | 20° | 0° | -20° | -40° | 40° | 20° | 0° | -20° | -40° | 40° | 20° | 0° | -20° | -40° | R22 is standard refrigerant
0.15625 | 0.19 | 0.14 | 0.11 | 0.08 | 0.06 | 0.26 | 0.21 | 0.16 | 0.12 | 0.09 | 0.18 | 0.13 | 0.1 | 0.07 | 0.05 | — | — | — | — | — | 10 psi pressure drop, 30" length std, 100°liq
0.1875 | 0.4 | 0.3 | 0.23 | 0.17 | 0.13 | 0.53 | 0.44 | 0.33 | 0.24 | 0.2 | 0.37 | 0.28 | 0.22 | 0.15 | 0.12 | 0.42 | 0.31 | 0.23 | 0.18 | 0.14
0.25 | 0.8 | 0.6 | 0.45 | 0.33 | 0.25 | 1.1 | 0.89 | 0.67 | 0.49 | 0.39 | 0.73 | 0.58 | 0.43 | 0.31 | 0.23 | 1.21 | 0.9 | 0.68 | 0.52 | 0.4
0.3125 | 1.6 | 1.2 | 0.9 | 0.66 | 0.5 | 2.2 | 1.7 | 1.3 | 0.98 | 0.79 | 1.5 | 1.1 | 0.83 | 0.62 | 0.46 | 2.46 | 1.83 | 1.39 | 1.06 | 0.81
0.375 | 2.8 | 2.1 | 1.6 | 1.2 | 0.88 | 3.7 | 2.9 | 2.2 | 1.7 | 1.4 | 2.5 | 2 | 1.5 | 1.1 | 0.8 | 4.44 | 3.32 | 2.51 | 1.91 | 1.47
tube size | r12 | 0.60667 | r22 |  | r404a |  | r410a
0.15625 | 0.19 | 0.19 | 0.26 | 0.32223 | 0.18 | 0.32223 |  | 0.32223
0.1875 | 0.4 | 0.092912 | 0.53 | 0.54853 | 0.37 |  | 0.42
0.25 | 0.8 | 0.10377 | 1.1 | 1.2531 | 0.73 |  | 1.21
0.3125 | 1.6 | 0.23289 | 2.2 | 2.3649 | 1.5 |  | 2.46
0.375 | 2.8 | 0.91294 | 3.7 | 3.9661 | 2.5 |  | 4.44